## Corrugated AL
SINGLE CORE 66 KV(E) XLPE CABLE WITH CORRUGATED ALUMINIUM SHEATH as per IS 7098-3
Nom. Area | Min. Thickness of Conductor Screen | Nom. Thickness of Insulation | Min. Thickness of Insulation Screen | Nom. Thickness of Al Sheath | Nom. Thickness of Outer Sheath | Approx. Overall Diameter | Approx Capacitance | Approx Charging Current | Short Circuit Rating of conductor for 1 sec
[9 empty] | ALUMINIUM | COPPER
(sqmm) | (mm) | (mm) | (mm) | (mm) | (mm) | (mm) | (mF/km) | (A/km) | (kA) | (kA)
240 | 0.8 | 11 | 0.8 | 1.7 | 2.8 | 66 | 0.19 | 2.2 | 22.56 | 34.32
300 | 0.8 | 11 | 0.8 | 1.7 | 2.8 | 68 | 0.2 | 2.4 | 28.2 | 42.9
400 | 0.8 | 11 | 0.8 | 1.7 | 3 | 72 | 0.22 | 2.6 | 37.6 | 57.2
500 | 0.8 | 11 | 0.8 | 1.7 | 3 | 75.5 | 0.24 | 2.9 | 47 | 71.5
630 | 0.8 | 11 | 0.8 | 1.7 | 3.2 | 79 | 0.26 | 3.1 | 59.22 | 90.09
800 | 0.8 | 11 | 0.8 | 1.7 | 3.4 | 86.5 | 0.3 | 3.6 | 75.2 | 114.4
1000 | 0.8 | 11 | 0.8 | 1.7 | 3.4 | 90 | 0.32 | 3.8 | 94 | 143
Fault Rating of Aluminium sheath is 31.5 KA for 1 Second

## POLY AL
SINGLE CORE 66 KV(E) XLPE/ARMOURED CABLE WITH POLY-ALUMINIUM & COPPER WIRE SCREEN as per IS 7098-3
Nom. Area | Min. Thickness of Conductor Screen | Nom. Thickness of Insulation | Min. Thickness of Insulation Screen | Nom. Area Of Copper Screen | Min. Thickness of Inner Sheath | Nom. Dia of Aluminium Armour Wire | Nom. Thickness of Outer Sheath | Approx. Overall Diameter | Max Capacitance | Max Charging Current | Short Circuit Rating of conductor for 1 sec
[11 empty] | ALUMINIUM | COPPER
(sqmm) | (mm) | (mm) | (mm) | (sqmm) | (mm) | (mm) | (mm) | (mm) | (Nom) | (Min) | (KA) | (KA)
240 | 0.8 | 11 | 0.8 | 209 | 1.1 | 2.5 | 2.2 | 64 | 0.19 | 2.2 | 22.56 | 34.32
300 | 0.8 | 11 | 0.8 | 209 | 1.1 | 2.5 | 2.36 | 66.5 | 0.2 | 2.4 | 28.2 | 42.9
400 | 0.8 | 11 | 0.8 | 209 | 1.2 | 2.5 | 2.36 | 68.5 | 0.22 | 2.6 | 37.6 | 57.2
500 | 0.8 | 11 | 0.8 | 209 | 1.2 | 3.15 | 2.52 | 73 | 0.24 | 2.9 | 47 | 71.5
630 | 0.8 | 11 | 0.8 | 209 | 1.2 | 3.15 | 2.68 | 76.5 | 0.26 | 3.1 | 59.22 | 90.09
800 | 0.8 | 11 | 0.8 | 209 | 1.3 | 3.15 | 2.84 | 84 | 0.3 | 3.6 | 75.2 | 114.4
1000 | 0.8 | 11 | 0.8 | 209 | 1.4 | 3.15 | 2.84 | 88 | 0.32 | 3.8 | 94 | 143
Fault Rating of Copper Wire is 31.5 KA for 1 Second