## 3C_HT-Arm
THREE CORE 6.6 KV (E) XLPE INSULATED ARMOURED CABLES
Thickness / Dimensions / Dia (mm)
Nom. Area | Insulation | Conductor Screen | Insulation Screen | Copper Tape | Inner Sheath | Round Wire Armoured |  |  | Flat Strip Armoured
[6 empty] | Armour Wire | Outer Sheath | Overall Diameter | Armour strip | Outer Sheath | Overall Diameter
(sqmm) | (Nom) | (Min) | (Min) | (Approx. ) | (Min) | (Nom) | (Min) | (Approx.) | (Nom) | (Min) | (Approx.)
25 | 2.8 | 0.3 | 0.3 | 0.03 | 0.4 | 2 | 1.72 | 38.5 | 0.8 | 1.56 | 36
35 | 2.8 | 0.3 | 0.3 | 0.03 | 0.4 | 2 | 1.72 | 41 | 0.8 | 1.72 | 38.5
50 | 2.8 | 0.3 | 0.3 | 0.03 | 0.5 | 2 | 1.88 | 44 | 0.8 | 1.72 | 41
70 | 2.8 | 0.3 | 0.3 | 0.03 | 0.5 | 2 | 1.88 | 47.5 | 0.8 | 1.88 | 45
95 | 2.8 | 0.3 | 0.3 | 0.03 | 0.5 | 2.5 | 2.04 | 52.5 | 0.8 | 1.88 | 48.5
120 | 2.8 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 56 | 0.8 | 2.04 | 52
150 | 2.8 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 59 | 0.8 | 2.2 | 55.5
185 | 2.8 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.36 | 62.5 | 0.8 | 2.2 | 59
240 | 2.8 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.52 | 69.5 | 0.8 | 2.36 | 64.5
300 | 3 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 74.5 | 0.8 | 2.52 | 69.5
400 | 3.3 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 85 | 0.8 | 2.84 | 78
500 | 3.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 93.5 | 0.8 | 3 | 87
630 | 3.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 99 | 0.8 | 3 | 93
THREE CORE 11 KV (E) XLPE INSULATED ARMOURED CABLES
Thickness / Dimensions / Dia (mm)
Nom. Area | Insulation | Conductor Screen | Insulation Screen | Copper Tape | Inner Sheath | Round Wire Armoured |  |  | Flat Strip Armoured
[6 empty] | Armour Wire | Outer Sheath | Overall Diameter | Armour strip | Outer Sheath | Overall Diameter
(sqmm) | (Nom) | (Min) | (Min) | (Approx. ) | (Min) | (Nom) | (Min) | (Approx.) | (Nom) | (Min) | (Approx.)
25 | 3.6 | 0.3 | 0.3 | 0.03 | 0.4 | 2 | 1.72 | 42 | 0.8 | 1.72 | 39.5
35 | 3.6 | 0.3 | 0.3 | 0.03 | 0.5 | 2 | 1.88 | 45 | 0.8 | 1.72 | 42.5
50 | 3.6 | 0.3 | 0.3 | 0.03 | 0.5 | 2.5 | 2.04 | 48.5 | 0.8 | 1.88 | 45
70 | 3.6 | 0.3 | 0.3 | 0.03 | 0.5 | 2.5 | 2.04 | 52.5 | 0.8 | 1.88 | 48.5
95 | 3.6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 56.5 | 0.8 | 2.04 | 52.5
120 | 3.6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 59.5 | 0.8 | 2.2 | 56
150 | 3.6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.36 | 62.5 | 0.8 | 2.2 | 59
185 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.52 | 68 | 0.8 | 2.36 | 63
240 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 73 | 0.8 | 2.52 | 68
300 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.84 | 77.5 | 0.8 | 2.68 | 72.5
400 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 86 | 0.8 | 2.84 | 79.5
500 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 94 | 0.8 | 3 | 87.5
630 | 3.6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 99.5 | 0.8 | 3 | 93
THREE CORE 11 KV (UE) XLPE INSULATED ARMOURED CABLES
Thickness / Dimensions / Dia (mm)
Nom. Area | Insulation | Conductor Screen | Insulation Screen | Copper Tape | Inner Sheath | Round Wire Armoured |  |  | Flat Strip Armoured
[6 empty] | Armour Wire | Outer Sheath | Overall Diameter | Armour strip | Outer Sheath | Overall Diameter
(sqmm) | (Nom) | (Min) | (Min) | (Approx. ) | (Min) | (Nom) | (Min) | (Approx.) | (Nom) | (Min) | (Approx.)
25 | 5.5 | 0.3 | 0.3 | 0.03 | 0.5 | 2.5 | 2.04 | 52 | 0.8 | 1.88 | 48.5
35 | 5.5 | 0.3 | 0.3 | 0.03 | 0.5 | 2.5 | 2.2 | 55 | 0.8 | 2.04 | 51
50 | 5.5 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 57.5 | 0.8 | 2.2 | 54
70 | 5.5 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.36 | 61.5 | 0.8 | 2.2 | 57.5
95 | 5.5 | 0.3 | 0.3 | 0.03 | 0.6 | 3.15 | 2.52 | 66.5 | 0.8 | 2.36 | 61.5
120 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.52 | 69.5 | 0.8 | 2.36 | 64.5
150 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 73 | 0.8 | 2.52 | 68
185 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.84 | 77 | 0.8 | 2.68 | 72
240 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 3 | 82 | 0.8 | 2.84 | 77
300 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 87.5 | 0.8 | 3 | 81.5
400 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 94.5 | 0.8 | 3 | 88
500 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 102 | 0.8 | 3 | 96
630 | 5.5 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 108 | 0.8 | 3 | 101.5
THREE CORE 22 KV (E) XLPE INSULATED ARMOURED CABLES
Thickness / Dimensions / Dia (mm)
Nom. Area | Insulation | Conductor Screen | Insulation Screen | Copper Tape | Inner Sheath | Round Wire Armoured |  |  | Flat Strip Armoured
[6 empty] | Armour Wire | Outer Sheath | Overall Diameter | Armour strip | Outer Sheath | Overall Diameter
(sqmm) | (Nom) | (Min) | (Min) | (Approx. ) | (Min) | (Nom) | (Min) | (Approx.) | (Nom) | (Min) | (Approx.)
35 | 6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.2 | 57 | 0.8 | 2.04 | 53.5
50 | 6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.36 | 60 | 0.8 | 2.2 | 56
70 | 6 | 0.3 | 0.3 | 0.03 | 0.6 | 2.5 | 2.36 | 63.5 | 0.8 | 2.36 | 60
95 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.52 | 69 | 0.8 | 2.36 | 64
120 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 72 | 0.8 | 2.52 | 67
150 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 75 | 0.8 | 2.68 | 70.5
185 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.84 | 79 | 0.8 | 2.68 | 74
240 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 86 | 0.8 | 2.84 | 79
300 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 90 | 0.8 | 3 | 83.5
400 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 96.5 | 0.8 | 3 | 90
500 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 104.5 | 0.8 | 3 | 98
630 | 6 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 110 | 0.8 | 3 | 103.5
THREE CORE 33 KV (E) XLPE INSULATED ARMOURED CABLES
Thickness / Dimensions / Dia (mm)
Nom. Area | Insulation | Conductor Screen | Insulation Screen | Copper Tape | Inner Sheath | Round Wire Armoured |  |  | Flat Strip Armoured
[6 empty] | Armour Wire | Outer Sheath | Overall Diameter | Armour strip | Outer Sheath | Overall Diameter
(sqmm) | (Nom) | (Min) | (Min) | (Approx. ) | (Min) | (Nom) | (Min) | (Approx.) | (Nom) | (Min) | (Approx.)
50 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.68 | 74 | 0.8 | 2.52 | 69
70 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 2.84 | 78 | 0.8 | 2.68 | 73
95 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 3.15 | 3 | 82 | 0.8 | 2.84 | 77
120 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 86.5 | 0.8 | 2.84 | 80
150 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 89.5 | 0.8 | 3 | 83
185 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 93 | 0.8 | 3 | 86.5
240 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 98 | 0.8 | 3 | 91.5
300 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 102 | 0.8 | 3 | 95.5
400 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 108.5 | 0.8 | 3 | 102.5
500 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 116.5 | 0.8 | 3 | 110
630 | 8.8 | 0.3 | 0.3 | 0.03 | 0.7 | 4 | 3 | 122 | 0.8 | 3 | 115.5