## Solar-IS 17293 (Class 2)
SOLAR CABLES AS PER IS 17293
Brief constructional details -
Voltage grade - 1500 V (DC)
Conductor material - Stranded Annealed Tinned Copper (Class-2)
Conductor shape - Stranded Compacted Circular
Insulation - XLPO
Outer sheath - XLPO
1500 V (DC) SOLAR CABLES TO IS 17293 (for Class 2 Conductors)
Nom. Area | Nom. Thickness of Insulation | Nom. Thickness of Outer Sheath | Mean Overall Diameter | Minimum Insulation Resistance at 20°C | Minimum Insulation Resistance at 90°C
(sqmm) | (mm) | (mm) | (mm) | (MΏ-km) | (MΏ-km)
16 | 0.7 | 0.9 | 9.5 | 374 | 0.374
25 | 0.9 | 1 | 11.8 | 384 | 0.384
35 | 0.9 | 1.1 | 13.2 | 327 | 0.327
50 | 1 | 1.2 | 15.1 | 317 | 0.317
70 | 1.1 | 1.2 | 17.3 | 291 | 0.291
95 | 1.1 | 1.3 | 19.6 |  | 0.251
120 | 1.2 | 1.3 | 21.6 | 244 | 0.244
150 | 1.4 | 1.4 | 24 | 254 | 0.254
185 | 1.6 | 1.6 | 27 | 261 | 0.261
240 | 1.7 | 1.7 | 30.4 | 243 | 0.243
300 | 1.8 | 1.8 | 33.5 | 231 | 0.231
400 | 2 | 2 | 37.7 | 227 | 0.227

## Solar-IS 17293 (Class 5)
SOLAR CABLES AS PER IS 17293
Brief constructional details -
Voltage grade - 1500 V (DC)
Conductor material - Flexible Annealed Tinned Copper (Class-5)
Conductor shape - Flexible Circular
Insulation - XLPO
Outer sheath - XLPO
1500 V (DC) SOLAR CABLES TO IS 17293 (for Class 5 Conductors)
Nom. Area | Nom. Thickness of Insulation | Nom. Thickness of Outer Sheath | Mean Overall Diameter | Minimum Insulation Resistance at 20°C | Minimum Insulation Resistance at 90°C
(sqmm) | (mm) | (mm) | (mm) | (MΏ-km) | (MΏ-km)
1.5 | 0.7 | 0.8 | 5.4 | 1050 | 1.05
2.5 | 0.7 | 0.8 | 5.9 | 862 | 0.862
4 | 0.7 | 0.8 | 6.6 | 709 | 0.709
6 | 0.7 | 0.8 | 7.2 | 610 | 0.61
10 | 0.7 | 0.8 | 8.3 | 489 | 0.489
16 | 0.7 | 0.9 | 9.8 | 393 | 0.393
25 | 0.9 | 1 | 12.2 | 395 | 0.395
35 | 0.9 | 1.1 | 14 | 335 | 0.335
50 | 1 | 1.2 | 16.3 | 314 | 0.314
70 | 1.1 | 1.2 | 18.7 | 291 | 0.291
95 | 1.1 | 1.3 | 20.8 | 258 | 0.258
120 | 1.2 | 1.3 | 23 | 249 | 0.249
150 | 1.4 | 1.4 | 25.7 | 260 | 0.26
185 | 1.6 | 1.6 | 28.7 | 268 | 0.268
240 | 1.7 | 1.7 | 32.3 | 249 | 0.249
300 | 1.8 | 1.8 | 35.6 | 237 | 0.237
400 | 2 | 2 | 40.6 | 230 | 0.23

## Solar-IS 17293 (CR)
SOLAR CABLES AS PER IS 17293
Brief constructional details -
Voltage grade - 1500 V (DC)
Conductor material - Stranded (Class-5) / Flexible (Class-5) Annealed Tinned Copper
Insulation - XLPO
Outer sheath - XLPO
Current Carrying Capacity of PV Cables
Nom. Area | Current Carrying Capacity According to Method of Installation
| Single cable free in air | Single cable on a surface | Two loaded cables touching, on a surface
(sqmm) | (mm) | (mm) | (MΏ-km)
1.5 | 28 | 27 | 22
2.5 | 38 | 36 | 30
4 | 52 | 49 | 41
6 | 66 | 63 | 53
10 | 89 | 87 | 73
16 | 120 | 118 | 97
25 | 167 | 158 | 126
35 | 207 | 196 | 156
50 | 261 | 248 | 190
70 | 329 | 313 | 245
95 | 394 | 374 | 298
120 | 462 | 440 | 348
150 | 537 | 510 | 401
185 | 611 | 581 | 460
240 | 735 | 698 | 545
300 | 831 | 788 | 631
400 | 999 | 947 | 751